## Sheet1
Simulation result by running the idf files that contains the HVAC system and all three floors. We select Mid-floor HVAC system sizing result as a reference, since the ground floor in this model has exterior floor. One thing was noticed that in the original one-floor model, it was using the ground floor as the one floor, so the plug load has elevator and it also has a few doors. Other than that, everything else is identifical with the middle floor. I think we should update the plug load for the elevator to be zero and keep the doors as it is.
Note that the zones are not order alphabetically.
AirTerminal:SingleDuct:VAV:Reheat
| Design Size Maximum Air Flow Rate [m3/s] | Design Size Constant Minimum Air Flow Fraction | User-Specified Constant Minimum Air Flow Fraction | Design Size Minimum Air Flow Rate [m3/s] | Design Size Maximum Flow per Zone Floor Area during Reheat [m3/s-m2] | Design Size Maximum Flow Fraction during Reheat []
CORE_MID VAV BOX COMPONENT | 2.11 | 0.35485 | 0.3499 | 0.73899 | 0.000751 | 0.3499
PERIMETER_MID_ZN_3 VAV BOX COMPONENT | 0.56664 | 0.27882 | 0.3 | 0.16999 | 0.00082 | 0.3
PERIMETER_MID_ZN_2 VAV BOX COMPONENT | 0.77721 | 0.12869 | 0.3 | 0.23316 | 0.001776 | 0.3
PERIMETER_MID_ZN_1 VAV BOX COMPONENT | 0.82868 | 0.19066 | 0.3 | 0.2486 | 0.001199 | 0.3
PERIMETER_MID_ZN_4 VAV BOX COMPONENT | 0.76635 | 0.13051 | 0.3 | 0.2299 | 0.001752
Coil:Heating:Electric
Design Size Nominal Capacity [W]
CORE_MID VAV BOX REHEAT COIL | 24101.91
PERIMETER_MID_ZN_3 VAV BOX REHEAT COIL | 12755.56
PERIMETER_MID_ZN_2 VAV BOX REHEAT COIL | 8391.12
PERIMETER_MID_ZN_1 VAV BOX REHEAT COIL | 12928.79
PERIMETER_MID_ZN_4 VAV BOX REHEAT COIL | 8505.89
AirLoopHVAC
| Sum of Air Terminal Maximum Heating Flow Rates [m3/s] | Sum of Air Terminal Minimum Heating Flow Rates [m3/s] | Sum of Air Terminal Maximum Flow Rates [m3/s] | Adjusted Heating Design Air Flow Rate [m3/s] | Adjusted Cooling Design Air Flow Rate [m3/s] | Adjusted Main Design Air Flow Rate [m3/s] | User Heating Air Flow Ratio [] | Calculated Heating Air Flow Ratio [] | Design Supply Air Flow Rate [m3/s]
PACU_VAV_MID | 1.62 | 1.62 | 5.05 | 1.9 | 4.32 | 4.32 | 0.3 | 0.43873 | 4.32
User-Specified values were used. Design Size values were used if no User-Specified values were provided.
Controller:OutdoorAir
Maximum Outdoor Air Flow Rate [m3/s]
PACU_VAV_MID_OA_CONTROLLER | 4.32
Coil:Cooling:DX:TwoSpeed
| Design Size High Speed Rated Air Flow Rate [m3/s] | Design Size High Speed Gross Rated Total Cooling Capacity [W] | Design Size High Speed Rated Sensible Heat Ratio | Design Size Low Speed Rated Air Flow Rate [m3/s] | Design Size Low Speed Gross Rated Total Cooling Capacity [W] | User-Specified Low Speed Gross Rated Sensible Heat Ratio
PACU_VAV_MID_COOLC DXCOIL | 4.32 | 102700.15 | 0.71503 | 1.44 | 34229.96 | 0.69
User-Specified values were used. Design Size values were used if no User-Specified values were provided.
Coil:Heating:Fuel
Design Size Nominal Capacity [W]
PACU_VAV_MID_HEATC | 45601.18
User-Specified values were used. Design Size values were used if no User-Specified values were provided.
Fan:VariableVolume
Design Size Maximum Flow Rate [m3/s]
PACU_VAV_MID FAN | 4.32
User-Specified values were used. Design Size values were used if no User-Spe
Report: Outdoor Air Details
For: Entire Facility
Timestamp: 2021-10-11 23:27:49
Mechanical Ventilation Parameters by Zone
| AirLoop Name | Average Number of Occupants | Nominal Number of Occupants | Zone Volume [m3] | Zone Area [m2] | Design Zone Outdoor Airflow - Voz [m3/s] | Minimum Dynamic Target Ventilation - Voz-dyn-min [m3/s]
CORE_MID | PACU_VAV_MID | 23.02 | 52.94 | 2698.04 | 983.54 | 0 | 0.425
PERIMETER_MID_ZN_3 | PACU_VAV_MID | 4.85 | 11.16 | 568.77 | 207.34 | 0 | 0.09
PERIMETER_MID_ZN_2 | PACU_VAV_MID | 3.07 | 7.07 | 360.08 | 131.26 | 0 | 0.057
PERIMETER_MID_ZN_1 | PACU_VAV_MID | 4.85 | 11.16 | 568.77 | 207.34 | 0 | 0.09
PERIMETER_MID_ZN_4 | PACU_VAV_MID | 3.07 | 7.06 | 360.05 | 131.25 | 0 | 0.057
Zone Ventilation Calculations for Cooling Design
| AirLoop Name | Box Type | Zone Primary Airflow - Vpz [m3/s] | Zone Discharge Airflow - Vdz [m3/s] | Minimum Zone Primary Airflow - Vpz-min [m3/s] | Zone Outdoor Airflow Cooling - Voz-clg [m3/s] | Primary Outdoor Air Fraction - Zpz | Primary Air Fraction - Ep | Secondary Recirculation Fraction- Er | Supply Air Fraction- Fa | Mixed Air Fraction - Fb | Outdoor Air Fraction - Fc | Zone Ventilation Efficiency - Evz
CORE_MID | PACU_VAV_MID | AIRTERMINAL:SINGLEDUCT:VAV:REHEAT | 2.112 | 2.112 | 0.739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.34991
PERIMETER_MID_ZN_3 | PACU_VAV_MID | AIRTERMINAL:SINGLEDUCT:VAV:REHEAT | 0.5666 | 0.5666 | 0.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.30004
PERIMETER_MID_ZN_2 | PACU_VAV_MID | AIRTERMINAL:SINGLEDUCT:VAV:REHEAT | 0.7772 | 0.7772 | 0.2332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.30005
PERIMETER_MID_ZN_1 | PACU_VAV_MID | AIRTERMINAL:SINGLEDUCT:VAV:REHEAT | 0.8287 | 0.8287 | 0.2486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.29999
PERIMETER_MID_ZN_4 | PACU_VAV_MID | AIRTERMINAL:SINGLEDUCT:VAV:REHEAT | 0.7663 | 0.7663 | 0.2299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0.30001
System Ventilation Calculations for Cooling Design
| Sum of Zone Primary Airflow - Vpz-sum [m3/s] | System Primary Airflow - Vps [m3/s] | Sum of Zone Discharge Airflow - Vdz-sum [m3/s] | Sum of Min Zone Primary Airflow - Vpz-min [m3/s] | Zone Outdoor Airflow Cooling - Voz-clg [m3/s] | Zone Ventilation Efficiency - Evz-min
PACU_VAV_MID | 5.0509 | 4.3204 | 5.0509 | 1.6207 | 0 | 1
Zone Ventilation Calculations for Heating Design
| AirLoop Name | Box Type | Zone Primary Airflow - Vpz [m3/s] | Zone Discharge Airflow - Vdz [m3/s] | Minimum Zone Primary Airflow - Vpz-min [m3/s] | Zone Outdoor Airflow Heating - Voz-htg [m3/s] | Primary Outdoor Air Fraction - Zpz | Primary Air Fraction - Ep | Secondary Recirculation Fraction- Er | Supply Air Fraction- Fa | Mixed Air Fraction - Fb | Outdoor Air Fraction - Fc | Zone Ventilation Efficiency - Evz
CORE_MID | PACU_VAV_MID | AIRTERMINAL:SINGLEDUCT:VAV:REHEAT | 0.739 | 0.739 | 0.739 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
PERIMETER_MID_ZN_3 | PACU_VAV_MID | AIRTERMINAL:SINGLEDUCT:VAV:REHEAT | 0.17 | 0.17 | 0.17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
PERIMETER_MID_ZN_2 | PACU_VAV_MID | AIRTERMINAL:SINGLEDUCT:VAV:REHEAT | 0.2332 | 0.2332 | 0.2332 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
PERIMETER_MID_ZN_1 | PACU_VAV_MID | AIRTERMINAL:SINGLEDUCT:VAV:REHEAT | 0.2486 | 0.2486 | 0.2486 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
PERIMETER_MID_ZN_4 | PACU_VAV_MID | AIRTERMINAL:SINGLEDUCT:VAV:REHEAT | 0.2299 | 0.2299 | 0.2299 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
System Ventilation Calculations for Heating Design
| Sum of Zone Primary Airflow - Vpz-sum [m3/s] | System Primary Airflow - Vps [m3/s] | Sum of Zone Discharge Airflow - Vdz-sum [m3/s] | Sum of Min Zone Primary Airflow - Vpz-min [m3/s] | Zone Outdoor Airflow Heating - Voz-htg [m3/s] | Zone Ventilation Efficiency - Evz-min
PACU_VAV_MID | 1.6207 | 1.6207 | 1.6207 | 1.6207 | 0 | 1